## Slide 1: Descriptive and inferential statistical methodologies have proven effective in creating a proactive ‘alarm’, accurately identifying Pump Failures with Horse Power (HP) and Pump Efficiency (PE) emerging as key variables of interest with deviations of 15 HP and > 3 % PE being our core signal thresholds.
Note: We’ve included a sample headline for you – you can feel free to use this or modify this as you see fit
Chart: Statistical Alarm Plot
Chart: Correlation Coefficient Pump Failure (Stdev)
| Horse Power | Volumetric Flow Meter 1 | Pump Efficiency | Volumetric Flow Meter 2 | Pump Speed (RPM) | Ambient Temperature | Pump Torque
 | 0.6901 | 0.64488 | 0.64355 | 0.62592 | 0.62456 | 0.60005 | 0.59726

## Slide 2: Descriptive Analysis has enabled us to clearly identify particular signature abnormalities showing clear signature changes in both Rolling Standard Deviation and Rolling Mean Datasets when observed over the respective failure period of interest.
Note: We’ve included a sample headline for you – you can feel free to use this or modify this as you see fit
Chart: Time Series Performance
Chart: Time Series Performance

## Slide 3: Further segmentation of the data via binary means (Pump Failure = 0 or 1) illustrated through mean and stdev charts, show a clear signature difference between that of normal behaviour and that of Failure with Raw (Pump Failure =1), Rolling Mean (Pump Failure =1), Rolling Stdev(Pump Failure =1) showing the 3 largest variances.
Note: We’ve included a sample headline for you – you can feel free to use this or modify this as you see fit

## Slide 4: Correlation analyses across datasets yield interesting insights with Volumetric Flow Meter 1 and Volumetric Flow Meter 2 negatively correlated with Pump Failure in the Rolling Mean Data, whilst Volumetric Flow Meter 1 and Volumetric Flow Meter 2 show a subsequently strong positive correlation in the Rolling Stdev Dataset.
Note: We’ve included a sample headline for you – you can feel free to use this or modify this as you see fit
Chart: Correlation Coefficient Pump Failure (Raw)
| Horse Power | Pump Speed (RPM) | Pump Torque | Ambient Temperature | Volumetric Flow Meter 1 | Pump Efficiency | Volumetric Flow Meter 2
 | 0.42184 | 0.26001 | 0.23318 | 0.20801 | -0.10249 | -0.10268 | -0.11211
Chart: Correlation Coefficient Pump Failure (Stdev)
| Horse Power | Volumetric Flow Meter 1 | Pump Efficiency | Volumetric Flow Meter 2 | Pump Speed (RPM) | Ambient Temperature | Pump Torque
 | 0.6901 | 0.64488 | 0.64355 | 0.62592 | 0.62456 | 0.60005 | 0.59726

## Slide 5: Lastly, analysis of the model fit reveals that with a R Squared of 0.77, a linear model is a good fit for the data with variables Horse Power, Pump Efficiency and Volumetric Flow Meter 2 having the largest coefficients, indicative that these variables have the most immediate relationship with respect to Pump Failure behaviour.
Chart: Coefficient Ranking
| Horse Power | Pump Efficiency | Volumetric Flow Meter 1 | Ambient Temperature | Pump Speed (RPM) | Pump Torque | Intercept | Volumetric Flow Meter 2
 | 0.76489 | 0.34235 | 0.050961 | 0.018224 | -0.017875 | -0.018903 | -0.035775 | -0.61136